11/18/2020 comments on ANSI/TIA-568.5, Balanced Single Twisted-Pair Telecommunications Cabling and Components Standard
Draft 1.6b

industry ballot.  Comments due 1/18/2021

E: editorial, T: technical, TN: technical no vote issue	Please do not re-size table

ID: Company with comment # (do not automate comment #)

| Page | Line | Clause | E/T/TN | ID | Comment (rationale) | Proposed change (specific; add, delete. From-to) | Resolution |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 56 | Table of contents | T | PAN-13 | Add ELTCTL reference to match the spec change from TCTL to ELTCTL when referencing measurement configurations with cabling involved (PL, Channel, cable). Aligns with PAN-8, PAN-9, PAN-10. | Change: “Channel TCTL” “Permanent link TCTL” “Cable TCTL” To: “Channel ELTCTL” “Permanent link ELTCTL” “Cable ELTCTL” And lines 74, 89 | Editor: Depending on resolution of ELTCTL comments |
| 2 | 140 | List of Tables | T | PAN-14 | Add ELTCTL reference to match the spec change from TCTL to ELTCTL when referencing measurement configurations with cabling involved (PL, Channel, cable). Aligns with PAN-8, PAN-9, PAN-10. | Change: “Channel TCTL” “Permanent link TCTL” “Cable TCTL” To: “Channel ELTCTL” “Permanent link ELTCTL” “Cable ELTCTL” And lines 141, 154, 155, 169, and 170 | Editor: Depending on resolution of ELTCTL comments |
| 3 | 203 | List of figures | T | PAN-15 | Add ELTCTL reference to match the spec change from TCTL to ELTCTL when referencing measurement configurations with cabling involved (PL, Channel, cable). Aligns with PAN-8, PAN-9, PAN-10. | Change: “Figure A.2 - Laboratory test configuration for cable and channel insertion loss, return loss, TCL, TCTL, ELTCTL, and | Editor: Depending on resolution of ELTCTL comments |
| 14 | 511 | 5.3.5 | T | SI-04 | The values are reasonable and we can remove the TBD’s now. | Delete TBD’s on line 511 and 512 (2 instances) | Editor: Recommend accept |
|  | 511 | 5.3.5 | T | CS-03 | To prepare for publication | Sweep through the document searching for TBDs and delete them as appropriate. | Editor: Defer to end |
| 17 | 610 | 6.1.1 | T | Prysmian1 | Drop absorbing clamp method: as it is not suitable for the specified frequency range | Delete txt with strikethrough: Coupling attenuation for single pair cabling shall be measured, over the specified frequency range of the cabling category, in accordance with IEC 62153-4-7 or IEC 62153-4-9 when using the triaxial method for components and cabling. ; or in accordance with IEC 62153-4-5 or IEC 62153-4-14 when using the absorbing clamp method for components and cabling. | Editor: Discuss. Comment text does not show strike throughs. Accommodated by PAN-07? |
| 17 | 614 | 6.1.1 | T | PAN-07 | Absorbing clamp method does not apply to frequencies below 30MHz. SPE specs currently are limited to an upper frequency of 20 MHz. Therefore, the absorbing clamp test method does not apply, and should be eliminated as a reference and accepted test for single pair. We should only spec the triaxial tube method. And we should eliminate references to absorbing clamp method. | Change: “Coupling attenuation for single pair cabling shall be measured, over the specified frequency range of the cabling category, in accordance with IEC 62153-4-7 or IEC 62153-4-9 when using the triaxial method for components and cabling; or in accordance with IEC 62153-4-5 or IEC 62153-4-14 when using the absorbing clamp method for components and cabling.” To: “Coupling attenuation for single pair cabling shall be measured, over the specified frequency range of the cabling category, in accordance with IEC 62153-4-7 or IEC 62153-4-9 when using the triaxial method for components and cabling.” | Editor: Discuss. Recommend accept |
| 18 | 665 | 6.3.1 | T | Prysmian2 | The CH limit of 61.5 ohms for SP1-400 looks to be incorrect. As it stands, we need 18AWG cable to meet this. Limit should be in the order of 120-150 ohms. | Change limit from 61.5 ohms to 150 ohms | Editor: 1000m DCR based on 10 connectors and 18AWG cable. 400m DCR based on 5 connectors and 23AWG cable. The current values appear to be correct. |
| 19 | 683 | 6.3.7 | T | SI-05 | This is no longer true now that we split the SP1-400 into a different equation. This information is not needed, and is not included in other parameters. | Delete Lines 683-690 | Editor: Consider with CS-04 |
|  | 683 | 6.3.7 | T | CS-04 | Since we changed the SP1-400 IL requirement this sentence is no longer true and needs to be updated. | From: SP1-1000 and SP1-400 single pair channel insertion loss limits are derived from equation (8)’ To: The channel insertion loss requirement for SP1-1000 is derived in equation (8). SP1-400 is derived in a similar way. | Editor: Consider with SI-05. |
| 20 | 702 | 6.3.7 | T | SI-06 | Notes 2 and 3 are no longer true and should be removed. | Delete Lines 702-706 | Editor: Recommend accept |
|  | 702 | 6.3.7 | T | CS-05 | These notes are no longer true, since we changed the SP1-400 requirement. | Delete notes 2 and 3 which are no longer true. | Editor: Recommend accept |
| 21 | 708 | 6.3.8 | T | Prysmian4 | Add a new TCL limit for shielded channels. Coupling attenuation defines the performance for a shielded solution, balance is less critical. | Add TCL limit: For Shielded Channels: 27 – 10log(f/100) with cap of 37dB Make existing limit for UTP only | Editor: Discuss. |
| 21 | 710 | 6.3.8 | TN | PAN-01 | Shielded systems have coupling attenuation to make sure signal radiation is limited. Shielded systems should not be held to the same strict TCL criteria. The stricter balance criteria provides no application benefit while adding unneeded complexity to the production process. In this case Panduit proposes a relaxation of balance parameter for shielded systems to align with current 4 pair cabling standards from TIA-568.2-D. | Change: “Calculations that result in single pair channel TCL values greater than 46 dB shall revert to a requirement of 46 dB minimum.” To: “For unshielded systems, calculations that result in single pair channel TCL values greater than 46 dB shall revert to a requirement of 46 dB minimum. For shielded systems, calculations that result in single pair channel TCL values greater than 37 dB shall revert to a requirement of 37 dB minimum.” On Table 9: Change existing SP1 specification to say: “SP1 (Unshielded)” Add another row that says: “SP1 (Shielded)”, and use the following equation for the TCL (dB): 37-20*log(f) (TBD) On Table 10: Change existing SP1 specification to say: “SP1 (Unshielded)” Add another column that says: “SP1 (Shielded)” and use the equation above for the values. Thru 718 | Editor: Discuss. Prysmian equation uses 27-10log(f)/100, Panduit equation uses 37-20log(f). |
|  | 716 | 6.3.8 | T | CS-06 | It is more challenging to meet TCL and TCTL requirements with a shielded, than an unshielded, cable. Relaxing the cable, and cabling, requirements, by 10 dB, will give useful relief, while not compromising system quality or integrity. | Add sentence ‘The TCL requirement for screened channels shall be relaxed by 10 dB from this requirement.’ | Editor: Consider with PAN-01 and Prysmian4. |
| 21-22 | 719 | 6.3.9 | TN | PAN-02 | Shielded systems have coupling attenuation to make sure signal radiation is limited. Shielded systems should not be held to the same strict TCTL criteria. The stricter balance criteria provides no application benefit while adding unneeded complexity to the production process. In this case Panduit proposes a relaxation of balance parameter for shielded systems to align with current 4 pair cabling standards from TIA-568.2-D. | Change: “TCTL values greater than 46 dB shall revert to a requirement of 46 dB minimum.” To: “For unshielded systems, TCTL values greater than 46 dB shall revert to a requirement of 46 dB minimum. For shielded systems, TCTL values greater than 32 dB shall revert to a requirement of 32 dB minimum.” On Table 11: Change existing SP1 specification to say: “SP1 (Unshielded)” Add another row that says: “SP1 (Shielded)”, and use the following equation for the TCTL (dB): 32-20*log(f) (TBD) On Table 12: Change existing SP1 specification to say: “SP1 (Unshielded)” Add another column that says: “SP1 (Shielded)” and use the equation above for the values. Thru 728 | Editor: Discuss. Editor feels that same limits should be used for TCL and TCTL. |
| 21 | 719 | 6.3.9 | T | PAN-08 | Cable losses need to be accounted for when specifying differential to common mode conversion losses. This impacts channels, permanent link, and cables. Change all TCTL references in section 6.3.9 to ELTCTL | In section 6.3.9: Change: TCTL To: ELTCTL Thru 728 | Editor: Discuss. Editor feels that cable losses are low at low frequencies and can be neglected. Cable loss for common mode and differential mode is different. Makes calculations unnecessarily complicated for no benefit. |
| 21 | 719 | 6.3.9 | T | Prysmian5 | Replace TCTL with ELTCTL. Specifying a limit for TCTL results in different channel performance depending on the insertion loss of the channel | Keep existing equation? 47 – 15log(f) with cap of 46dB | Editor: Discuss. Editor feels that cable losses are low at low frequencies and can be neglected. Cable loss for common mode and differential mode is different. Makes calculations unnecessarily complicated for no benefit. |
| 21 | 719 | 6.3.9 | T | Prysmian6 | Add a new ELTCTL limit for shielded channels. Coupling attenuation defines the performance for a shielded solution, balance is less critical. | Add ELTCTL limit: For Shielded Channels: 32 – 20log(f) with cap of 32dB Make existing limit for UTP only | Editor: Discuss. Editor feels that cable losses are low at low frequencies and can be neglected. Cable loss for common mode and differential mode is different. Makes calculations unnecessarily complicated for no benefit. |
|  | 725 | 6.3.9 | T | CS-07 | It is more challenging to meet TCL and TCTL requirements with a shielded, than an unshielded, cable. Relaxing the cable, and cabling, requirements, by 10 dB, will give useful relief, while not compromising system quality or integrity. | dd sentence ‘The TCTL requirement for screened channels shall be relaxed by 10 dB from this requirement.’ | Editor: Propose accept in principle consider with Panduit and Prysmian comments. |
| 23 | 758 | 6.3.15 | T | SI-07 | Missing the 2 MHz table entry. | Add 2 MHz value of 56.0 to Table 17 | Editor: Propose accept. |
| 25 | 785 | 6.5.1 | T | Prysmian3 | The PL limit of 53.7 ohms for SP1-400 looks to be incorrect. As it stands, we need 18AWG cable to meet this. Limit should be in the order 120-150 ohms. | Change limit from 53.7 ohms to 147 ohms | Editor: Current value is based on 350m of 23 AWG and four connectors and is correct. |
| 26 | 804 | 6.5.7 | T | SI-08 | This is no longer true now that we split the SP1-400 into a different equation. This information is not needed, and is not included in other parameters. | Delete Lines 804-812 | Editor: Propose accept. |
|  | 804 | 6.5.7 | T | CS-08 | Since we changed the SP1-400 IL requirement this sentence is no longer true and needs to be updated. | From ‘SP1’ to “SP1-1000” Add The requirement for SP1-400 is derived in a similar way.’ | Editor: Consider with SI-08. |
| 26 | 815 | 6.5.7 | T | SI-09 | Feel it is OK to remove the TBD at this time. | Delete: TBD | Editor: Propose accept. |
| 26 | 822 | 6.5.7 | T | SI-10 | Notes 2 and 3 are no longer true and should be removed. | Delete Lines 822-827 | Editor: Propose accept. |
|  | 822 | 6.5.7 | T | CS-09 | This note is no longer true, for SP1-400. | Delete note 2 | Editor: Propose accommodated by SI-10 |
| 27 | 828 | 6.5.8 | TN | PAN-03 | Align permanent link TCL specifications with channel specifications noted in PAN-01. | Change: “Calculations that result in single pair permanent link TCL values greater than 46 dB shall revert to a requirement of 46 dB minimum.” To: “For unshielded systems, calculations that result in single pair permanent link TCL values greater than 46 dB shall revert to a requirement of 46 dB minimum. For shielded systems, calculations that result in single pair permanent link TCL values greater than 37 dB shall revert to a requirement of 37 dB minimum.” On Table 23: Change existing SP1 specification to say: “SP1 (Unshielded)” Add another row that says: “SP1 (Shielded)”, and use the following equation for the TCL (dB): 37-20*log(f) (TBD) On Table 24: Change existing SP1 specification to say: “SP1 (Unshielded)” Add another column that says: “SP1 (Shielded)” and use the equation above for the values. Thru 837 | Editor: Discuss |
| 27 | 828 | 6.5.8 | T | Prysmian7 | Add a new TCL limit for shielded links. Coupling attenuation defines the performance for a shielded solution, balance is less critical. | Add TCL limit: For Shielded Links: 27 – 10log(f/100) with cap of 37dB Make existing limit for UTP only | Editor: Discuss |
|  | 835 | 6.5.8 | T | CS-09 | It is more challenging to meet TCL and TCTL requirements with a shielded, than an unshielded, cable. Relaxing the cable, and cabling, requirements, by 10 dB, will give useful relief, while not compromising system quality or integrity. | Add sentence ‘The TCL requirement for screened permanent links shall be relaxed by 10 dB from this requirement.’ | Editor: Propose accept in principle consider with Panduit and Prysmian comments. |
| 27-28 | 838 | 6.5.9 | TN | PAN-04 | Align permanent link TCTL specifications with channel specifications noted in PAN-02. | Change: “TCTL values greater than 46 dB shall revert to a requirement of 46 dB minimum.” To: “For unshielded systems, TCTL values greater than 46 dB shall revert to a requirement of 46 dB minimum. For shielded systems, TCTL values greater than 32 dB shall revert to a requirement of 32 dB minimum.” On Table 25: Change existing SP1 specification to say: “SP1 (Unshielded)” Add another row that says: “SP1 (Shielded)”, and use the following equation for the TCTL (dB): 32-20*log(f) (TBD) On Table 26: Change existing SP1 specification to say: “SP1 (Unshielded)” Add another column that says: “SP1 (Shielded)” and use the equation above for the values. Thru 845 | Editor: Discuss |
| 27 | 838 | 6.5.9 | T | Prysmian8 | Replace TCTL with ELTCTL. Specifying a limit for TCTL results in different link performance depending on the insertion loss of the link | Keep existing equation? 47 – 15log(f) with cap of 46dB | Editor: same rationale as for channel. |
| 27 | 838 | 6.5.9 | T | Prysmian9 | Add a new ELTCTL limit for shielded links. Coupling attenuation defines the performance for a shielded solution, balance is less critical. | Add ELTCTL limit: For Shielded links: 32 – 20log(f) with cap of 32dB Make existing limit for UTP only | Editor: same rationale as for channel. |
| 27 | 839 | 6.5.9 | T | PAN-09 | Cable losses need to be accounted for when specifying differential to common mode conversion losses. This impacts channels, permanent link, and cables. Change all TCTL references in section 6.5.9 to ELTCTL | In section 6.5.9: Change: TCTL To: ELTCTL Thru 845 | Editor: same rationale as for channel. |
|  | 842 | 6.5.9 | T | CS-10 | It is more challenging to meet TCL and TCTL requirements with a shielded, than an unshielded, cable. Relaxing the cable, and cabling, requirements, by 10 dB, will give useful relief, while not compromising system quality or integrity. | Add sentence ‘The TCTL requirement for screened permanent links shall be relaxed by 10 dB from this requirement.’ | Editor: Propose accept in principle consider with Panduit and Prysmian comments. |
| 29 | 874 | 6.5.15 | T | SI-11 | Missing the 2 MHz table entry. | Add 2 MHz value of 56.0 to Table 31 | Editor: Accept |
| 31 | 918 | 6.6.6 | T | Prysmian10 | Propose to remove TBD and accept limit for SP1-400 | Accept limit for SP1-400 | Editor: Propose accept |
| 32 | 918 | 6.6.6 | T | SI-12 | Feel it is OK to remove the TBD at this time. | Delete: TBD | Editor: Propose accept |
|  | 918 | 6.6.6 | T | CS-11 | Since the text implies requirements over the range of 20-60 C, the table needs to specify the temperature at which it applies. The text also gives instructions to modify the requirements for different temperatures. | Change title of table 36 to ‘cable insertion loss at 20 C’ | . Editor: Propose accept |
| 32 | 922 | 6.6.7 | T | Prysmian11 | Add a new TCL limit for shielded cables. Coupling attenuation defines the performance for a shielded solution, balance is less critical. | Add TCL limit: For Shielded cables: 30 – 10log(f/100) with cap of 40dB Make existing limit for UTP only | Editor: Editor believes that TCL and TCTL limits should be the same. |
| 32-33 | 923 | 6.6.7 | TN | PAN-05 | Align cable TCL specifications with channel specifications noted in PAN-01. | Change: “Calculations that result in single pair cable TCL values greater than 50 dB shall revert to a requirement of 50 dB minimum.” To: “For unshielded systems, calculations that result in single pair cable TCL values greater than 50 dB shall revert to a requirement of 50 dB minimum. For shielded systems, calculations that result in single pair permanent link TCL values greater than 40 dB shall revert to a requirement of 40 dB minimum.” On Table 38: Change existing SP1 specification to say: “SP1 (Unshielded)” Add another row that says: “SP1 (Shielded)”, and use the following equation for the TCL (dB): 40-20*log(f) (TBD) On Table 39: Change existing SP1 specification to say: “SP1 (Unshielded)” Add another column that says: “SP1 (Shielded)” and use the equation above for the values. Thru 933 | Editor: Discuss |
|  | 930 | 6.6.7 | T | CS-12 | It is more challenging to meet TCL and TCTL requirements with a shielded, than an unshielded, cable. Relaxing the cable, and cabling, requirements, by 10 dB, will give useful relief, while not compromising system quality or integrity. | Add sentence ‘The TCL requirement for screened cables shall be relaxed by 10 dB from this requirement.’ | Editor: Propose accept in principle consider with Panduit and Prysmian comments. |
| 33 | 934 | 6.6.8 | TN | PAN-06 | Align cable TCTL specifications with channel specifications noted in PAN-02. | Change: “Calculations that result in single pair cable TCTL values greater than 50 dB shall revert to a requirement of 50 dB minimum.” To: “For unshielded systems, calculations that result in single pair cable TCTL values greater than 50 dB shall revert to a requirement of 50 dB minimum. For shielded systems, TCTL values greater than 35 dB shall revert to a requirement of 35 dB minimum.” On Table 40: Change existing SP1 specification to say: “SP1 (Unshielded)” Add another row that says: “SP1 (Shielded)”, and use the following equation for the TCTL (dB): 35-20*log(f) (TBD) On Table 41: Change existing SP1 specification to say: “SP1 (Unshielded)” Add another column that says: “SP1 (Shielded)” and use the equation above for the values. Thru 942 | Editor: Discuss |
| 33 | 934 | 6.6.8 | T | PAN-10 | Cable losses need to be accounted for when specifying differential to common mode conversion losses. This impacts channels, permanent link, and cables. Change all TCTL references in section 6.6.8 to ELTCTL | In section 6.6.8: Change: TCTL To: ELTCTL Thru 944 | Editor: Same consideration as for channel. |
| 33 | 934 | 6.6.8 | T | Prysmian12 | Replace TCTL with ELTCTL. Specifying a limit for TCTL results in different performance depending on the insertion loss of the cable | Keep existing equation? 50 – 15log(f) with cap of 50dB | Editor: Same consideration as for channel. |
| 33 | 934 | 6.6.8 | T | Prysmain13 | Add a new ELTCTL limit for shielded cables. Coupling attenuation defines the performance for a shielded solution, balance is less critical. | Add ELTCTL limit: For Shielded cables: 35 – 20log(f) with cap of 35dB Make existing limit for UTP only | Editor: Same consideration as for channel. |
|  | 940 | 6.6.8 | T | CS-13 | It is more challenging to meet TCL and TCTL requirements with a shielded, than an unshielded, cable. Relaxing the cable, and cabling, requirements, by 10 dB, will give useful relief, while not compromising system quality or integrity. | Add sentence ‘The TCTL requirement for screened cables shall be relaxed by 10 dB from this requirement.’ | Editor: Propose accept in principle consider with Panduit and Prysmian comments. |
| 33 | 942 | 6.6.8 | T | SI-13 | Missing the 2 MHz table entry. | Add 2 MHz value of 45.5 to Table 41 | Editor: Accept |
| 35 | 973 | 6.6.14 | T | SI-14 | Missing the 2 MHz table entry. | Add 2 MHz value of 56.0 to Table 46 | Editor: Accept |
|  | 1024 | 6.8.9 table 52 | T | CS-18 | There are wrong values in the informative table. | The values at 8, 10, 16, and 20 MHz sb 49.9, 48.0, 43.9, and 42.0, respectively. | Editor: Accept |
| 38 | 1029 | 6.8.10 | T | SI-15 | I think we changed the TCL and did not change the TCTL equation. TCL and TCTL for channel, link, and cable are the same. Why does connecting hardware have a more stringent TCTL requirement? Proposed equation also equals what is in IEC 63171-1. | Change equation to: 68-20*log(f) Update informative table 54. | Editor: Propose accept. |
|  | 1029 | 6.8.10 | T | CS-19 | I thought at least these were supposed to be the same, and that the TCL requirement was what it was supposed to be. | Change the connector TCTL requirement to be the same as the TCL. Change tables 53 and 54. | Editor: Accommodated by SI-15 |
|  | 1054 | 6.8.14 table 56 | T | CS-20 | To make the informative table more useful. | Extend the values in table 56 to one decimal place. | Editor: Accept |
| 42 | 1125 | A.2 | T | PAN-11 | Add ELTCTL reference to match the spec change from TCTL to ELTCTL when referencing measurement configurations with cabling involved (PL, Channel, cable). Aligns with PAN-8, PAN-9, PAN-10. | Change: “include insertion loss, return loss, TCL, TCTL, and delay.” To: “include insertion loss, return loss, TCL, TCTL, ELTCTL, and delay. | Editor: ELTCTL is not a measurement. It is a calculation. |
| 44 | 1176 | Figure A.2 | T | PAN-12 | Add ELTCTL reference to match the spec change from TCTL to ELTCTL when referencing measurement configurations with cabling involved (PL, Channel, cable). Aligns with PAN-8, PAN-9, PAN-10. | Change: “TCTL, and propagation delay” To: “TCTL, ELTCTL, and propagation delay” | Editor: ELTCTL is not a measurement. It is a calculation. |
|  | 1301 | C.2 figure C.2 | T | CS-22 | The graphic illustrating the channel is missing. | Restore the graphic. | Editor: Accept |
| 10 | 384 | 3.2 | E | SI-01 | This term is not used in the document | Delete: Line 384, definition for “coverage area” | Editor: Accept |
| 10 | 407 | 3.2 | E | SI-02 | This term is not used in the document | Delete: Lines 407-410, definition for “listed” | Editor: Accept |
| 13 | 497 | 5.3.2 | E | SI-03 | Proper wording | In Note 2, “Color” should not be capitalized | Editor: Accept |
|  | 497 | 5.3.2 Table 2 | E | CS-01 | There is only one option. | Delete ‘option 1’ | Editor: Accept |
|  | 502 | 5.3.3 | E | CS-02 |  | Place a full stop at the end. | Editor: Accept |
|  | 758 | 6.3.15 table 17 | E | CS-14 | Missing info | Add a line for 2 MHz 56.0 | Editor: Accept |
|  | 874 | 6.5.15 Table 31 | E | CS-15 | Missing info | Add a line for 2 MHz 56.0 | Editor: Accept |
|  | 942 | 6.6.8 table 41 | E | CS-16 | Missing info | Add a line for 2 MHz 45.5 | Editor: Accept |
|  | 973 | 6.6.14 table 46 | E | CS-17 | Missing info | Add a line for 2 MHz 56.0 | Editor: Accept |
|  | 1162 | A.3 figure A.1 | E | CS-21 | The box ‘screen or shield’ is overlapping the box ‘test fixture’. |  | Editor: Accept |